CRESTRON® GREEN LIGHT® GL-IPAC MODULAR SWITCHING CONTROLS

The GL-IPAC-SW8 switching panel provides internal controls for 8 circuits of switched load and is expandable to support up to 64 circuits of switched load by adding external panels and switching modules. It features local inputs for sensors and keypads, along with a LCD user interface where installers or users can set up the system without having to connect to a computer.

The GL-IPAC-SW8 is perfect for smaller-sized installations, such as retail stores, small office spaces, parking garages, and service stations, which typically require only on/off switching—eliminating the need for a larger, more expensive panel. In addition, the GL-IPAC-SW8 can be easily integrated with Crestron automation solutions, for centralized monitoring and remote control of multiple locations.

Out-of-the-Box Lighting Control The GL-IPAC-SW8 comes preconfigured for use as the central control processor for a Crestron Green Light® Power Switching system. Right out of the box, the GL-IPAC-SW8 affords easy setup and programming for a complete switching system consisting of up to 64 switched loads, 16 local and two remote keypads, 24 occupancy and photo sensors, and 100 time clock events.

Keypads with as many as 12 buttons each can be programmed easily to control lighting loads and other functions. Lights can be programmed to turn on and off automatically using the built-in astronomical time clock feature. Lighting events may be programmed to occur at specific times or at an offset from sunrise or sunset. Occupancy sensors and photo sensors may also be implemented to enable automatic on/off lighting control based on room occupancy and ambient light levels.

Save Energy Built-in support for occupancy and photo sensors helps to strike a perfect balance between daylight harvesting and comfort, reducing energy costs. Automatically turn off lights in unoccupied areas and maintain balanced bulb brightness with the natural light level in the room. Crestron® GLS sensors can be placed strategically in each space to maximize the benefits of energy management.

Easy Deployment Packaged in one metal enclosure, the GL-IPAC-SW8 can be deployed in small spaces, including plenum ceilings. The surface-mount GL-IPAC-SW8 can be affixed to a wall or ceiling rafter, cleanly out of sight. Standard wire-entry knockouts are provided.

Crestron is the world's leading manufacturer of advanced control and automation systems, innovating technology and reinventing the way people live and work. Offering integrated solutions to control audio, video, computer, IP and environmental systems, Crestron streamlines technology, improving the quality of life for people in corporate boardrooms, conference rooms, classrooms, auditoriums, and in their homes.

Specifier: The Specifier/Design Professional is responsible for the accuracy of all project specifications, including system application and coordination with related sections.  This guide specification is provided as a convenience and requires editing to match actual project requirements.  CRESTRON ELECTRONICS, INC. SHALL NOT BE LIABLE FOR ANY DAMAGES ARISING OUT OF THE USE OF ANY OF ITS GUIDE SPECIFICATIONS.  For Crestron design assistance and design review please contact Sales Support Services Department at   800.237.2041 or techsales@crestron.com.

Crestron®, Green Light®, and RoomView® are registered trademarks of Crestron Electronics, Inc.

SECTION 26 09 43.13
DIGITAL-NETWORK LIGHTING CONTROLS

GENERAL

SUMMARY

Specifier:  Edit paragraph and subparagraphs below to correspond to components required for this Project.

Section Includes:

Modular, self-contained lighting [and equipment] control system with multiple presets.

Related Information:

Specifier:  Related Information paragraph is optional.  If retaining, edit and coordinate list of sections below to correspond to Project requirements.

Division 12 Section "Window Treatments" for window treatments controlled by modular dimming control system.

Division 25 Section "Integrated Automation Control of Electrical Systems" for software and integration hardware for network lighting controls.

Division 26 Section "Common Work Results For Electrical".

Division 26 Section "Wiring Devices".

Division 26 Section "Lighting Devices" for occupancy sensors controlled by modular dimming control system.

Division 26 Section "Interior Lighting" for light fixtures controlled by modular dimming control system.

Division 27 Section "Communications Horizontal Cabling" for communications cabling requirements for modular dimming control system.

Division 27 Section "Audio-Visual Communications" for communications and network cabling requirements for lighting systems and over all control systems communications.

REFERENCES

National Fire Protection Association (NFPA):

NFPA 70 - National Electrical Code.

SYSTEM DESCRIPTION

Specifier:  Edit description below to correspond to Project requirements.

Microprocessor-based, modular solid-state switching device utilizing preset control software, in an integrated control system including the following:

Lighting Controller System:  Concealed mounting, self contained, multichannel controller with user-adjustable relay and equipment controls with network and expansion capabilities:

Integrated lighting and switching controls.

Lighting controller system integrates the following separate controls:

Native communication with building wide Audio Visual Systems.

Keypad controls.

Touch panel controls.

Window treatment controls.

Remote occupancy sensors.

Room-combining partition sensor.

Lighting load shedding.

Timed room lighting.

Daylight compensating lighting controls.

Audio visual equipment controls.

Interface to facility-wide room management.

Interface to building automation system interface.

Slaved Controllers:  Remote slaved controllers allowing master lighting controller system to control lighting circuits, and circuit loads, while emulating the function of the connected lighting controller system control channel.

Unified System Integration – Controller supports native communication protocol utilized by the AV control system.

Communication protocol adaptors or translation interfaces between AV control system and lighting control system will not be accepted.

ACTION SUBMITTALS

Specifier:  Action submittals require responsive action by A/E or Owner.

Product Data:  For each type of product required for complete modular lighting control system, demonstrating compliance with requirements.

Shop Drawings:  Indicate the following:

Schematic diagram of controlled circuits and motorized equipment actuators.

Circuits and emergency circuits with capacity and phase, control zones, load type and voltage per circuit.

INFORMATIONAL SUBMITTALS

Specifier:  Informational submittals require review, but not response, by A/E or Owner.  Edit list below based on project requirements.

Sample of manufacturer's warranty.

Load Measurement Report:  Submit field test report of finished lighting circuit work.

CLOSEOUT SUBMITTALS

Operating and maintenance instructions.

QUALITY ASSURANCE

Manufacturer Qualification:  Manufacturer of modular controls with minimum [five] years record of satisfactory manufacturing and support of components comparable to basis of design system.

Source Requirements:  Provide modular lighting controls hardware and software through a single source from a single manufacturer.

Specifier:  Retain paragraph below if Owner allows substitutions but requires strict control over qualifying of substitutions.

Manufacturer Qualifications:  Approved manufacturer of modular lighting controls listed in this Section with minimum [five] years record of satisfactory manufacturing and support of components comparable to basis of design system.

Approval of Comparable Products:  Submit the following in accordance with project substitution requirements, within time allowed for substitution review:

Product data indicating compliance with requirements of this Section.

Samples of each component.

Sample submittals from similar project.

Project references:  Minimum of 5 completed installations, with Owner and Architect contact information.

Sample warranty.

Substitutions following award of contract are not allowed except as stipulated in Division 01 General Requirements.

Approved manufacturers must comply with separate requirements of Submittals Article.

Electrical Components, Devices, and Accessories:  UL listed and labeled.

Regulatory Requirements:  Provide components and systems that comply with requirements of the following:

NFPA 70.

Underwriters Laboratory (UL) standards.

Applicable codes and regulations.

COORDINATION

Specifer:  Edit list below to reference sections controlled by modular lighting controls for Project.  Crestron GL-IPAC-SW8 system is able to integrate with Crestron's Cresnet building-wide automation network, BAS, building security systems, and a variety of equipment and devices.

Coordinate integrated lighting controls with systems and components specified in the following sections:

Division 11 Section "Audio-Visual Equipment".

Division 12 Section "Window Treatments".

Division 23 Section "Instrumentation and Control for HVAC".

Division 25 Section "Integrated Automation Control of Electrical Systems".

Division 26 Section "Wiring Devices".

Division 26 Section "Lighting Devices".

Division 26 Section "Interior Lighting".

Division 27 Section "Communications Horizontal Cabling".

Division 28 Section "Electronic Access Control and Intrusion Detection".

PROJECT CONDITIONS

Environmental Conditions Range:

Temperature: 32 – 104  deg F (0 - 40 deg C).

Relative Humidity:  10 – 90 percent, noncondensing.

WARRANTY

Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of modular lighting controls system the fail in materials or workmanship within the specified warranty period following substantial completion.

Warranty Period:  Touch screen display and overlay components:  90 days.

Warranty Period:  Disc drives and other moving parts, pan/tilt heads, and power supplies:  1 year.

Warranty Period:  Other components, 3 years.

Manufacturer's Extended Support Service:  Extended telephone support:  Unlimited period.

PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  Subject to compliance with requirements, provide products of Crestron Electronics, Inc., Rockleigh, NJ 07647,  Phone (800)237-2041, Fax: (201)767-1903, www.crestron.com [or comparable products from a single manufacturer approved by Architect prior to bidding], with the following components and characteristics.

MULTI-ROOM LIGHTING CONTROLLER [WITH POWER MANAGEMENT]

Lighting Controller:  Integrated lighting, and equipment switching control system panel, in metal enclosure for mounting in concealed space.

Basis of Design Product: Crestron, Greenlight GL-IPAC-SW8 Integrated Lighting System, Model GL-IPAC-SW8.

Lighting Controller System Characteristics:  Provide pre-configured lighting controller, with capabilities for manual setup, and software setup through programming port, configured as follows in layout indicated:

[Stand-alone controller] [Multiple-slaved controllers] [Controller networked to central lighting control processor specified in Division 26 Section ["Central Dimming Controls"] ["Network Lighting Controls"].

Switched Load Types:

Fluorescent ballast.

Incandescent.

Magnetic low voltage.

Electronic low voltage.

Neon/Cold cathode.

High-Intensity discharge.

Motors.

Power Requirements:

Main Power:  120 – 277 VAC, 50/60 Hz.

Available Network Power:  15W at 24VDC.

Input/Output:

Line Power Inputs:  8 terminal blocks, 2 connections per channel, paralleled.

Switch Channel Outputs: 8 terminal blocks.

Enclosure:  Surface-mounted industrial control enclosure suitable for concealed locations, 14.13 by 12.13 by 4.06 inch (308 by 359 by 104 mm).

SYSTEM ACCESSORIES

Specifier:  Retain and edit accessory paragraphs below as required to match system requirements.

Specifier:  Cameo Series Keypads are available in 12 designer colors in 2- to 6- button arrays.  Faceplates are not furnished by Crestron.

Remote Keypad Controls:  Field-configurable remote keypad with auto-adjusting backlight illuminating replaceable, engravable programmable buttons in number indicated, with white LED indicators, configured to fit in standard single-gang box.

          - Basis of Design:  Crestron, Cameo Series Keypad Model C2N-CB (D/F) Series.

          - Color:  As selected from manufacturer's full range of minimum 12 colors.

          - Faceplates: [Insert faceplate description].

Specifier:  Designer Series Keypads are available with backlit black buttons or standard white or ivory buttons in 2, 4, 6, 8, or 12- button arrays.  Textured finish integrated faceplates or optional architectural faceplates are available.

Remote Keypad Controls:  Remote keypad with[ backlight illuminating] replaceable, engravable buttons in number indicated, with amber LED indicators, configured to fit in standard single-gang box.

          - Basis of Design:  Crestron, Designer Series Keypad Model CNX- Series.

          - Faceplates: [As selected from manufacturer's full line] [Insert faceplate description].

Specifier:  Decorator Series Keypads are available with black, white, or ivory buttons in 6, 8, or 12- button arrays.  Faceplates are not furnished by Crestron.

Remote Keypad Controls:  Remote keypad with replaceable, engravable buttons in number indicated, with red LED indicators, 3W, configured to fit in standard single-gang box.

          - Basis of Design:  Crestron, Decorator Series Keypad Model C2N-DB Series.

          - Faceplates:  [Insert faceplate description].

Specifier:  Crestron GLS-OIR Series Occupancy Sensors utilize passive infrared technology to achieve dependable motion detection with superior immunity to false triggering from air currents, inanimate objects, or movement in an adjacent corridor.  Advanced self-adaptive, passive infrared motion sensing affords excellent reliability for control of lighting, climate control and other devices in the room.  Sensitivity is adjustable for optimum performance.

Passive Infrared Occupancy Sensors:  Passive infrared detection with internal microprocessor.  Sensor independently adjustable for installed conditions.  Delayed time off adjustment.  Walk-through mode.  Adjustable built-in photocell for daylight optimization.  Equipped with 3-wire interface for direct connection to control system; 24 VDC power from network control bus.

Basis of Design:  Crestron Photocell Model GLS-OIR Series.

Mounting and Coverage:  [Low profile ceiling surface mounted, 360 deg., 450 sq. ft.] [Low profile ceiling surface mounted, 360 deg., 1500 sq. ft.] [Wall bracket mounted, 360 deg., 2500 sq. ft.] [Ceiling bracket mounted, 360 deg., 2500 sq. ft.] [As indicated].

Specifier:  Crestron GLS-ODT Series Occupancy Sensors offer dual-technology sensing utilizing both ultrasonic and passive infra-red detection with an internal microprocessor to maintain accurate control of lighting systems, reducing energy costs while maintaining user convenience.  Sensors detect movement within space while reducing false triggering or shutoffs while space is occupied.  Several mounting types and coverage areas are available.

Remote Occupancy Sensors:  Combination of ultrasonic motion detection and passive infrared detection with internal microprocessor.  Sensor independently adjustable for installed conditions.  Delayed time off adjustment.  Walk-through mode.  Adjustable built-in photocell for daylight optimization.  Equipped with 3-wire interface for direct connection to control system; 24 VDC power from network control bus.

Basis of Design:  Crestron Photocell Model GLS-ODT Series.

Coverage:  [180 deg., 500 sq. ft.] [360 deg., 1000 sq. ft.] [360 deg., 2000 sq. ft.] [1200 sq. ft.].

Mounting:  [Ceiling flush mounted] [Ceiling surface mounted] [Ceiling bracket mounted] [Wall flush mounted] [Wall surface mounted] [Wall bracket mounted] [As indicated].

Occupancy Sensor Interface Device:  Integrates occupancy sensors and related sensors with control network. In separate enclosure.  4-wire bus providing 24 VDC power to network devices, with two independent sensing inputs.

Basis of Design: Crestron Sensor Integration Module Model GLS-SIM.

Specifier:  Crestron Photocell Model GLS-LOL open-loop photocell sensing provides a cost-effective solution for daylight harvesting, allowing multiple lighting zones to be controlled by a single sensor. In a typical office, classroom, or similar space, the photocell is installed on the ceiling near a window, or in the light well of a skylight, directed toward the incoming daylight and away from any electrical lighting fixtures. The system estimates the total amount of ambient lighting in the room according to the light level measured by the photocell.

Requires use of control processor specified below.

Photocell Sensor, Open Loop Type:  Continually monitors daylight entering window or skylight to enable daylight harvesting applications to provide control of room lighting based on presence of daylight. Equipped with 3-wire interface for direct connection to control system utilizing control processor; 24 VDC power from network control bus.

          - Basis of Design: Crestron Photocell Model GLS-LOL.

          - Mounting:  [Ceiling flush mounted] [Ceiling surface mounted] [Wall flush mounted] [Wall surface mounted] [As indicated].

Specifier:  Crestron Photocell GLS-LCL is intended for use with closed-loop type daylight harvesting systems.  It continually monitors the total ambient light level from all available light sources, enabling precise control of room lighting and window shades to maintain a consistent level of light throughout the day. The best place to install the GLS-LCL in a typical office or similar space is on the ceiling directly above the primary work area. The sensor measures all light within a 60° cone, which consists predominately of reflected light, acquiring the most natural approximation of perceived changes in ambient light levels.

Requires use of control processor specified below.

Photocell Sensor, Closed Loop Type:  Continually monitors daylight at work station location to enable daylight harvesting applications to provide control of room lighting based on lighting level at workstation. Equipped with 3-wire interface for direct connection to control system utilizing control processor; 24 VDC power from network control bus.

          - Basis of Design: Crestron Photocell GLS-LCL.

          - Mounting:  [Ceiling flush mounted] [Ceiling surface mounted] [Wall flush mounted] [Wall surface mounted] [As indicated].

Power Supply:  50W, 24 V regulated power supply with 2: 4-pin network connectors, fuse-protected.

Basis of Design: Crestron Cresnet Power Supply Model GLA-PWS-50.

CONDUCTORS AND CABLING

Power Supply Side of Remote-Control Power Sources:  Comply with requirements of Division 26 Section "Low-Voltage Electrical Power Conductors."

UTP Cable:  100-ohm, UTP.  Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444 and NFPA 70 for the following types:

Communications Control Cable, Non-Plenum Rated:  22 AWG stranded bare copper data pair, and 18 AWG stranded bare copper power pair, Type CM.

Basis of Design Product:  Crestron CRESNET-NP.

Communications Control Cable, Plenum Rated:  22 AWG data pair, stranded bare copper and 18 AWG AWG power pair, stranded bare copper, Type CMP, complying with NFPA 262.

Basis of Design Product:  Crestron CRESNET-P.

Communications High-Power Control Cable, Non-Plenum Rated:  22 AWG stranded bare copper data pair, and 12 AWG stranded bare copper power pair, Type CM.

Basis of Design Product:  Crestron CRESNET-HP-NP.

EXECUTION

EXAMINATION

Prior to installation, examine work area to verify measurements, and that commencing installation complies with manufacturer's requirements.

INSTALLATION

Comply with requirements of Division 26 Sections "Common Work Results for Electrical."

Do not install lighting controls until space is enclosed, HVAC systems are running, and overhead and wet work in lighting control work space are complete.

Install lighting controls in accordance with manufacturer's instructions.

Grounding:  Provide electrical grounding in accordance with NFPA 70.

Perform setup for each lighting scene, window shade controller, and audio-visual equipment component.

SYSTEM STARTUP

Provide system startup and adjustment to occupied conditions in accordance with manufacturer's recommendations.

Perform operational testing to verify compliance with Specifications.  Adjust as required.

Measure and record load on each controlled circuit in each scene.  Submit report of load measurements.

CLOSEOUT ACTIVITIES

Specifier:  On projects with more complex installations, consider retaining both demonstration and training by manufacturer's authorized representative.  Consult Crestron representative for costs associated with these services.

Demonstration:  Schedule lighting controls demonstration with Owner to allow verification that lighting controls function as required.

Training:  Train Owner's personnel to operate, maintain, and program modular lighting controls.

END OF SECTION 26 09 43.13